## Input
From template version :-	1.053	MACROS UNLOCKED					This workbook is designed to create the data required for standard blocks. Put the device information into the "Input" sheet ( this sheet ), the "Create Data" button on this sheet should then be pressed. This will put data in the output sheets ( whose tabs are blue & cyan ). Simocode ¦ Profibus types are identified with a leading underscore. / The information ( formulae ) contained in Columns A,B,C,D,E,G,N & P of the Output sheets must extend beyond the anticipated maximum rows to be added ( any cell that has a coloured background ). / When you want to import into Step 7 - retrieve the information from P3 onwards you might need to change the name of the Data block. / The tabs highlighted red & pink in the workbook contain the templates for the data which will be created for each device of that type. If data structure required changes these can be edited. / If you want to import from S7 – then use the PASTE-SPECIAL option with-in Open Office. / ( Care must be used when handling the variable values – these are not changed during the running of the macros and therefore the values could relate to different rows – particular if the equipment list is changed ) / ( The Clear data macro buttons have been removed and instead at the end of the run of the Create Macros an additional ten lines of blanks are added – these should make the boundary between the new data and the old data easily visible ) / ( A sanity check is performed at the beginning of each macro run – to make sure that the data sheets marry up with the list of 'Types' on this page. ) / To collate entries you can use coloured blocks – or colours anywhere … / Type in any comment you want … ( If it hasn't got a TYPE then the contents of the row are ignored ) / You can't leave completely blank lines because they will be interpreted as the end of the list – and the macros will complete once it sees a blank entry in the Symbolic column.

			Last ran :-	7/11/2013

		Last ran :-	20/12/2013 12:23:54	06/01/2014 11:55:33	20/12/2013 15:40:46
				Available Types
			PLC Dbs	SCADA	Profibus ¦ Simocode
				HMI
		( FB58 )	PID	PID	_SIMOCODE
		( FB301 )	DOL	DOL	_SIMOCODE_REV
Datablock Numbers			DOL_REV	DOL_REV	_ALTIVAR
WTH – Words to HMI	360	( FB303 )	VSD	VSD	_PULSAR
BTH – Bits to HMI	361	( FB305 )	SOLENOID	SOLENOID	_EH_TMT184
WFH – Words from HMI	362	( FB306 )	DIG_ACTR	DIG_ACTR	_ABB_MAGMASTER
BFH – Bits from HMI	363	( FB307 )	ANLG_ACTR	ANLG_ACTR	_YOKAGAWA_pH
ALM – Alarm Data	309	( FB311 )	ANLG_INST	ANLG_INST	_YOKAGAWA_pH_Temp
DP1_IN	130	( FB312 )	DUAL_VAL	DUAL_VAL	_AUMA_DIG
DP1_OUT	131	( FB313 )	TRIPLE_VAL	TRIPLE_VAL	_AUMA_ANLG
DP2_IN	321	( FB314 )	DS	DS	_DIRIS_A40
DP2_OUT	322	( FB315 )	DSA	DSA	_PROSONIC
DP3_IN	323	( FB316 )	DSA1A2	DSA1A2	_AUMA_AC
DP3_OUT	324	( FB369 )	DIRIS	DIRIS	_ABB_WATERMASTER	= _ABB_PROCESSMASTER
DP4_IN	325		KWHR	KWHR	_ROTORK
DP4_OUT	326		DIG_DEV	DIG_DEV
DP5_IN	327		DA1A2	DA1A2
DP5_OUT	328		TOTALISER	TOTALISER
			SPECIFIC	SPECIFIC

PLC05 – Chemical					Profibus					States \ Ranges					Manufacturer
Symbolic	Description		PLC DB / Type	SCADA Type	Type	Network / 1 – 5	DP /	Station		For Digitals		For Analogues					VTC = Vendor to Confirm
				HMI Type			PA			State 0	State 1	Eng-Lo	Eng-Hi	Units
CP02	Incomer Power Meter		KWHR	KWHR	_DIRIS_A40	1	DP	11	1
A5_LIT315	Chemical Tank Level		ANLG_INST	ANLG_INST	_AUMA_ANLG	1	DP	12	2					Pulsar	0-3m
A5_LIT323	Blind Tank Level		ANLG_INST	ANLG_INST	_AUMA_ANLG	1	DP	13	3					Pulsar	0-3m
A5_P504	Chemical Dosing Pump		VSD	VSD	_SIMOCODE	1	DP	14	4					Grundfos
A5_P504	Chemical Dosing Pump				_ALTIVAR	1	DP	15	4					Grundfos
Instrumentation
A5_LS316	Chemical Tank High High Level		DIG_DEV	DIG_DEV					5	High High	Hlthy					Prominent
A5_AV508	Chemical Tank Outlet Valve		DIG_ACTR	DIG_ACTR					6					+GF+
A5_LS318	Chemical Dosing Pump PRV Catch Pot		DIG_DEV	DIG_DEV					7	Failed	Hlthy					Prominent
A5_FIT112	Chemical Dosing Pumps Delivery Flowmeter		ANLG_INST	ANLG_INST					8			0	625	l/hr		ABB
A5_LS319	Chemical Dosing Skid Drip Tray High Level		DIG_DEV	DIG_DEV					9	High	Hlthy					Prominent
A5_LS320	Chemical Dual Containment Catch Pot		DIG_DEV	DIG_DEV					10	Failed	Hlthy					Prominent
A5_LS321	Chemical Dosing Dual Containment Enclosure Level		DIG_DEV	DIG_DEV					11	Failed	Hlthy
A5_LS317	Chemical Tank High Level		DIG_DEV	DIG_DEV					12	High	Hlthy					Prominent
A5_XS201	Emergency Eyewash 1		DIG_DEV	DIG_DEV					13	Operated	Hlthy					Safety Shower Company
A5_XS202	Emergency Eyewash 2		DIG_DEV	DIG_DEV					14	Operated	Hlthy					Safety Shower Company
A5_XS203	Emergency Shower		DIG_DEV	DIG_DEV					15	Operated	Hlthy					Safety Shower Company
A5_LS322	Emergency Shower Low Level Switch		DIG_DEV	DIG_DEV					16	LowLevel	Hlthy
A5_LS324	Chemical Blind Tank High High		DIG_DEV	DIG_DEV					17	High High	Hlthy					Balfour Beatty
A5_TS601	Emergency Shower Low Temperature Switch		DIG_DEV	DIG_DEV					18	Low	Hlthy	-20	30	°C		Safety Shower Company – E & H
Anything	Anything		SPECIFIC	SPECIFIC